## Cover
P100 BMS RS485/RS232 Communication Protocol
Rev 1.0.1
HUNATE Co., ltd

## Revision History
Revision History
◆
REV | Date | Description
1.0.0 | 2024-11-02 | First
1.0.1 | 2024-11-12 | BMSDataTable "offset 59" ERRORCODE datatype change "bitfield32" to "UINT16" E014, E015 error code deleted, E014 : SM_F_BMIC_FAULT
1.0.2 | 2024-12-20 | The value of the EVT Table has been converted from decimal to hexadecimal according to the bitfield type.

## Protocol Overview
1. Overview
this protocol is a universal protocol for the RS485/RS232 Interface of BMS ( P100 )
▶ baudrate : 9600 bps, data- 8bit, stop bit - 1bit, No parity , No control
2. Frame Structure
2.1 HMI sends data
in the frame sent by HMI, a frame of data include 5 data areas such as frame header, slave address, command code, frame data, checksum. The frame format is shown in Table 1.
when Command Code is "Fault Erase Request", Refer "Random Seed" in received Data from BMS. The "Random seed" value is the input value required to calculate the "KEY value"
The "key value" is four digits, and each number represents a digit from 0 to 9.
To monitor whether the battery is currently charging or discharging, see "Pack ST" of Table 3.
Tabe 1. Send Frame Format
Frame Header |  | Slave Address | Command Code |  | Frame Data |  | Checksum
2byte |  | 1byte | 1byte |  | 2byte |  | 1byte
frame header |  | 2byte | fixed "0x07 0xE0"
Slave Address |  | 1byte | default is "0x01"
Command Code |  | 1byte | 0xFF - Data Request
0xF0 - FAULT ERASE Request
0xF1 - Capacity Configuration Request
Frame Data |  | 2byte | Command Code (0xFF) - 0x0000
Command Code (0xF0) - 0xXXXX ( key value )
Command Code (0xF1) - 0xXXXX ( Capacity )
Checksum |  | 1byte | D = B0^B1^B2^B3^B4^B5
▶ Command Code - "Data Request" Example
Offset |  | Cotent | type |  | len |  | Unit |  | Sample Data
0 |  | Frame Header | UINT16 |  | 2 |  | - |  | 0x07 0xE0
2 |  | Slave Address | UINT8 |  | 1 |  | - |  | 0x01
3 |  | Command Code | UINT8 |  | 1 |  | - |  | 0xFF
4 |  | Frame Data | UINT16 |  | 2 |  | - |  | 0x00 0x00
6 |  | CheckSum | UINT8 |  | 1 |  | - |  | 0x19
▶ Command Code - "Fault Erase Request" Example
Offset |  | Cotent | type |  | len |  | Unit |  | Sample Data
0 |  | Frame Header | UINT16 |  | 2 |  | - |  | 0x07 0xE0
2 |  | Slave Address | UINT8 |  | 1 |  | - |  | 0x01
3 |  | Command Code | UINT8 |  | 1 |  | - |  | 0xF0
4 |  | Frame Data | UINT16 |  | 2 |  | - |  | 0x12 0x34 ( 1234 )
6 |  | CheckSum | UINT8 |  | 1 |  | - |  | 0x30
▶ Command Code - "Capacity Configuration Request" Example
Offset |  | Cotent | type |  | len |  | Unit |  | Sample Data
0 |  | Frame Header | UINT16 |  | 2 |  | - |  | 0x07 0xE0
2 |  | Slave Address | UINT8 |  | 1 |  | - |  | 0x01
3 |  | Command Code | UINT8 |  | 1 |  | - |  | 0xF1
4 |  | Frame Data | UINT16 |  | 2 |  | - |  | 0x1 0x30 (304Ah)
6 |  | CheckSum | UINT8 |  | 1 |  | - |  | 0x26
2.2 BMS response
if BMS receive HMI data, check Slaved Address and Command Code.
if Slave Address is not "0x01", BMS don't response.
if Command Code is '0xFF", Frame Data is 64byte. if Command Code is "0xF0" , Frame Data is 2byte
Tabe 2. Response Frame Format
Frame Header |  | Slave Address | Command Code |  | Frame Data |  | Checksum
2byte |  | 1byte | 1byte |  | 2byte~66byte |  | 1byte
frame header |  | 2byte | fixed "0x07 0xEF"
Slave Address |  | 1byte | default is "0x01"
Command Code |  | 1byte | 0xFF - Data Request
0xF0 - FAULT ERASE Request
Frame Data |  | 66byte | Command Code (0xFF) - Table 3. BMS Data Table
|  | 2byte | Command Code (0xF0) - 0x1 or 0x2
|  | 2byte | Command Code (0xF1) - 0x1 or 0x2
Checksum |  | 1byte | D = B0^…^ End Byte of Fame Data
▶ Command Code (0xF0) - Response Frame Data
offset | Content |  | data type | len | factor | offset | min | max | unit | sample data
0 | KEY Validation |  | UINT16 | 2 | 1 | 0 | 1 | 2 | - | 1 - SUCCESS 2 - FAIL
▶ Command Code (0xF1) - Response Frame Data
offset | Content |  | data type | len | factor | offset | min | max | unit | sample data
0 | Capacity Configuration |  | UINT16 | 2 | 1 | 0 | 1 | 2 | - | 1 - SUCCESS 2 - FAIL
Table 3. BMS Data Table
▶ Command Code (0xFF) - Response Frame Data
offset | Content |  | data type | len | factor | offset | min | max | unit | sample data
0 | Total Battery Voltage |  | UINT16 | 2 | 10 | 0 | 0 | 65535 | 10mV | 0x99A * 10mV = 24.580V
2 | Pack Sensing Voltage |  | UINT16 | 2 | 10 | 0 | 0 | 65535 | 10mV | 0x99A * 10mV = 24.580V
4 | Current |  | INT16 | 2 | 10 | 0 | -32768 | 32767 | 10mA | 0xb1e0 * 10mA = -200.0A
6 | Power(W) |  | UINT16 | 2 | 1 | 0 | 0 | 65535 | w | 4800 = 4.8kw
8 | SOC |  | UINT8 | 1 | 1 | 0 | 0 | 100 | % | 5 = 5%
9 | CV1 |  | UIN16 | 2 | 1 | 0 | 0 | 65535 | mV | 3400 = 3.4V
11 | CV2 |  | UIN16 | 2 | 1 | 0 | 0 | 65535 | mV | 3400 = 3.4V
13 | CV3 |  | UIN16 | 2 | 1 | 0 | 0 | 65535 | mV | 3400 = 3.4V
15 | CV4 |  | UIN16 | 2 | 1 | 0 | 0 | 65535 | mV | 3400 = 3.4V
17 | CV5 |  | UIN16 | 2 | 1 | 0 | 0 | 65535 | mV | 3400 = 3.4V
19 | CV6 |  | UIN16 | 2 | 1 | 0 | 0 | 65535 | mV | 3400 = 3.4V
21 | CV7 |  | UIN16 | 2 | 1 | 0 | 0 | 65535 | mV | 3400 = 3.4V
23 | CV8 |  | UIN16 | 2 | 1 | 0 | 0 | 65535 | mV | 3400 = 3.4V
25 | CV9 |  | UIN16 | 2 | 1 | 0 | 0 | 65535 | mV | 3400 = 3.4V
27 | CV10 |  | UIN16 | 2 | 1 | 0 | 0 | 65535 | mV | 3400 = 3.4V
29 | CV11 |  | UIN16 | 2 | 1 | 0 | 0 | 65535 | mV | 3400 = 3.4V
31 | CV12 |  | UIN16 | 2 | 1 | 0 | 0 | 65535 | mV | 3400 = 3.4V
33 | CV13 |  | UIN16 | 2 | 1 | 0 | 0 | 65535 | mV | 3400 = 3.4V
35 | CV14 |  | UIN16 | 2 | 1 | 0 | 0 | 65535 | mV | 3400 = 3.4V
37 | CV15 |  | UIN16 | 2 | 1 | 0 | 0 | 65535 | mV | 3400 = 3.4V
39 | CV16 |  | UIN16 | 2 | 1 | 0 | 0 | 65535 | mV | 3400 = 3.4V
41 | Ext T1 |  | INT8 | 1 | 1 | 0 | -40 | 85 | °C | 0xd8 = -40°C
42 | Ext T2 |  | INT8 | 1 | 1 | 0 | -40 | 85 | °C | 0xd8 = -40°C
43 | Ext T3 |  | INT8 | 1 | 1 | 0 | -40 | 85 | °C | 0xd8 = -40°C
44 | Ext T4 |  | INT8 | 1 | 1 | 0 | -40 | 85 | °C | 0xd8 = -40°C
45 | Board T1 |  | INT8 | 1 | 1 | 0 | -40 | 85 | °C | 0xd8 = -40°C
46 | Board T2 |  | INT8 | 1 | 1 | 0 | -40 | 85 | °C | 0xd8 = -40°C
47 | Random Seed |  | UINT8 | 1 | 1 | 0 | 1 | 10 | - | Random Seed Key
48 | Pack ST |  | bitfield8 | 1 | 1 | 0 | 0 | 0xFF | - | BIT0 - OCV State BIT1 - Charge State BIT2 - Discharge State BIT3 - Full Charge State BIT4 - Full Discharge State BIT5 - PowerDown State BIT6 - ERROR State BIT7 - Permenant Fail State
49 | CellBal |  | bitfield16 | 2 | 1 | 0 | 0 | 0xFFFF | - | BIT0 - C1 Bal ON ~ BIT15 - C16 Bal ON
51 | StrEvt1 |  | bitfield32 | 4 | 1 | 0 | 0 | 0xFFFFFFFF | - | refer "EVT Table"
55 | StrEvt2 |  | bitfield32 | 4 | 1 | 0 | 0 | 0xFFFFFFFF | - | refer "EVT Table"
59 | ERROCODE |  | UINT16 | 2 | 1 | 0 | 0 | 0xFFFF |  | refer "ERROR Table"
61 | Reserved1 |  | UINT16 | 2
63 | Capacity |  | UINT16 | 2 | 100 | 0 | 0 | 65535 | 100mAh | 3040 * 100mAh = 304.0 Ah
65 | Reserved2 |  | UINT8 | 1

## EVT Table
▶ EVT Table
Type | Name | Code | Label | Description | Value
bitfield32 | StrEvt1 | COMMUNICATION_ERROR | Communication Error | Internal MCU Communication Error | 0x00000001
|  | OVER_TEMP_ALARM | Over Temperature Alarm | Over Temperature (Fault) | 0x00000002
|  | OVER_TEMP_WARNING | Over Temperature Warning | Over Temperature (Warning) | 0x00000004
|  | UNDER_TEMP_ALARM | Under Temperature Alarm | Under Temperature (Fault) | 0x00000008
|  | UNDER_TEMP_WARNING | Under Temperature Warning | Under Temperatur (Warning) | 0x00000010
|  | OVER_CHARGE_CURRENT_ALARM | Over Charge Current Alarm | Over Charge Current (Fault) | 0x00000020
|  | OVER_CHARGE_CURRENT_WARNING | Over Charge Current Warning | Over Charge Current (Warning) | 0x00000040
|  | OVER_DISCHARGE_CURRENT_ALARM | Over Discharge Current Alarm | Over Discharge Current (Fault) | 0x00000080
|  | OVER_DISCHARGE_CURRENT_WARNING | Over Discharge Current Warning | Over Discharge Current (Warning) | 0x00000100
|  | OVER_VOLT_ALARM | Over Voltage Alarm | Over Pack Voltage (Fault) | 0x00000200
|  | OVER_VOLT_WARNING | Over Voltage Warning | Over Pack Voltage (Warning) | 0x00000400
|  | UNDER_VOLT_ALARM | Under Voltage Alarm | Under Pack Voltage (Fault) | 0x00000800
|  | UNDER_VOLT_WARNING | Under Voltage Warning | Under Pack Voltage (Warning) | 0x00001000
|  | UNDER_SOC_MIN_ALARM | Under State of Charge Min Alarm | Unser SOC (Fault) | 0x00002000
|  | UNDER_SOC_MIN_WARNING | Under State of Charge Min Warning | Unser SOC (Warning) | 0x00004000
|  | OVER_SOC_MAX_ALARM | Over State of Charge Max Alarm | Over SOC (Fault) | 0x00008000
|  | OVER_SOC_MAX_WARNING | Over State of Charge Max Warning | Over SOC (Warning) | 0x00010000
|  | VOLTAGE_IMBALANCE_WARNING | Voltage Imbalance Warning | Cell Deviation ERROR | 0x00020000
|  | TEMPERATURE_IMBALANCE_ALARM | Temperature Imbalance Alarm | Temperature Deviation ERROR | 0x00040000
|  | TEMPERATURE_IMBALANCE_WARNING | Temperature Imbalance Warning | N/A | 0x00080000
|  | CONTACTOR_ERROR | Contactor Error | Relay ERROR | 0x00100000
|  | FAN_ERROR | Fan Error |  | 0x00200000
|  | GROUND_FAULT | Ground Fault Error |  | 0x00400000
|  | OPEN_DOOR_ERROR | Open Door Error |  | 0x00800000
|  | RESERVED_1 | Current Imbalance Warning |  | 0x01000000
|  | OTHER_ALARM | Other Battery Alarm |  | 0x02000000
|  | OTHER_WARNING | Other Battery Warning |  | 0x04000000
bitfield32 | StrEvt2 | OVER_CVOL_ALARM | Over Cell Voltage Alarm | Over Cell Voltage (FAULT) | 0x00000001
|  | OVER_CVOL_WARNING | Over Cell Voltage Warning | Over Cell Voltage (Warning) | 0x00000002
|  | UNDER_CVOL_ALARM | Under Cell Voltage Alarm | Under Cell Voltage(Fault) | 0x00000004
|  | UNDER_CVOL_WARNING | Under Cell Voltage Warning | Under Cell Voltage(Warning) | 0x00000008
|  | OCD_ALARM | Over Current DetectAlarm | Over Mass Current Detection (FAULT) | 0x00000010

## ERROR Table
▶ERROR CODE Table
ERROR TABLE
ERR NO | Description | Reboot | Resume Condition | Language (Korean)
E001 | COM ERROR | RELEASE | COM RECOVERY | 통신 에러
E002 | OTP | KEEP | ERROR ERASE | 고온 에러
E003 | UTP | RELEASE | Reboot | 저온 에러
E004 | OCCP | KEEP | ERROR ERASE | 과충전전류 에러
E005 | ODCP | KEEP | ERROR ERASE | 과방전전류 에러
E006 | OPVP | KEEP | ERROR ERASE | 과충전 에러
E007 | UPVP | KEEP | ERROR ERASE | 과방전 에러
E008 | CONTP | KEEP | Impossible | 컨텍터 에러
E009 | OCVP | KEEP | ERROR ERASE | 과충전셀전압 에러
E010 | UCVP | KEEP | ERROR ERASE | 과방전셀전압 에러
E011 | SM_EEPCHKSUM | KEEP | ERROR ERASE | 기타 에러
E012 | SM_MCUFAULT | KEEP | ERROR ERASE | 기타 에러
E013 | SM_VOLTAGE | KEEP | ERROR ERASE | 기타 에러
E014 | SM_BMIC_FAULT | KEEP | ERROR ERASE | 기타 에러
E015
E016
E017
E000 | unexpected error